## Slide 1: Fundamentals of Electric Transmission System Planning Short Course The Power System Modeling Process
Scott Dahman
PowerWorld Corporation
scott@powerworld.com
March 19-21, 2024
© copyright Scott Dahman, 2024

## Slide 2: Power System Modeling Introduction
The focus for this talk is on how planning engineers model the electric grid
The words model or modeling have lots of definitions. A useful definition here is
  "Modeling and simulation (M&S) is the use of a physical or logical representation of a given system to generate data and help determine decisions or make predictions about the system.”
Modeling is crucial for power system planning since we can’t (easily) physically build the system being considered
Definition source: whatis.techtarget.com/definition/modeling-and-simulation-MS

## Slide 3: Modeling Cautions
"All models are wrong, but some are useful," George Box, Empirical Model-Building and Response Surfaces, (1987, p. 424)
  Models are an approximation to reality, not reality, so they always have some degree of approximation
  Box went on to say that the practical question is how wrong to they have to be to not be useful
A good part of engineering is deciding what is the appropriate level of modeling, and knowing under what conditions the model will fail
Always keep in mind what problem you are trying to solve!
Of course, engineering often involves using widely accepted modeling and analysis approaches for common problems. Increasingly this requires adhering to particular standards
  Still, the engineer needs to know the conditions under which these approaches fail!

## Slide 4: Where We’ll Start: Major Power Grid Components
The distribution system is the source of most outages, but these are almost always small-scale events
Photo source: http://save-the-squirrels.com

## Slide 5: Energy and Power
Energy is A property of matter that quantifies its ability to perform useful work.
  Forms: kinetic, gravitational, heat, light, sound, magnetic, nuclear, chemical, and electric
  Units for energy: 1 MWh = 1000 kWh 1 kWh = 3.6 million Joules = 3412.14 Btu
Power is Energy on the move from form to form or place to place.
  Time derivative of energy as it is transferred
  Units for power: Watt (Volt-Ampere) kW = 1000 W, MW, GW, 1 Hp = 746 Watts
One gallon of gasoline has about 0.125 MBtu (36.5 kWh) of energy stored in chemical form
U.S. annual electric energy consumption is about 3600 billion kWh
  This is about 13,333 kWh per person, which means on average we each use 1.5 kW of power continuously
Installed U.S. generation capacity is about 1000 GW (about 3 kW per person)
A rule of thumb is one pound of coal can supply about 1 kWh (details are about 13,000 btu/lb, which implies about 26.2% all in efficiency)

## Slide 6: Review of phasors
The goal of phasor analysis is to simplify the analysis of constant frequency ac systems
v(t) = Vmax cos(wt + qv)
i(t) = Imax cos(wt + qI)
Root Mean Square (RMS) voltage of sinusoid

## Slide 7: Phasor representation
Euler’s Identity:
Phasor notation is developed by rewriting using Euler’s identity
(Note: |V| is the RMS voltage)

## Slide 8: Phasor representation, cont’d
(Note: Some texts use boldface type for complex numbers; some use overbars)
The RMS, cosine-referenced voltage phasor is:

## Slide 9: Power system notation
Power system components are usually shown as
“oneline diagrams.”
Large arrows are
used to show loads
Generators are
shown as circles
Transmission lines are shown as a single line
This makes more sense when considering three-phase systems

## Slide 10: Reactive compensation
Key idea of reactive compensation is to supply reactive power locally. In the previous example this can be done by adding a 16 Mvar capacitor at the load
Compensated circuit is identical to first example with just real power load
This problem was only easy to solve because the load voltage magnitude was assumed constant; in practice this is not the case and motivates the need for power flow algorithms

## Slide 11: Reactive compensation, cont’d
Reactive compensation decreased the line flow from 564 Amps to 400 Amps. This has advantages
  Lines losses, which are equal to I2 R decrease
  Lower current allows utility to use small wires, or alternatively, supply more load over the same wires
  Voltage drop on the line is less
Reactive compensation is used extensively by utilities
Capacitors can be used to “correct” a load’s power factor to an arbitrary value.

## Slide 12: Power factor correction example

## Slide 13: Distribution system capacitors

## Slide 14: Balanced Three-Phase () Systems
A balanced three-phase () system has
  three voltage sources with equal magnitude, but with an angle shift of 120
  equal loads on each phase
  equal impedance on the lines connecting the generators to the loads
Bulk power systems are almost exclusively 3
Single-phase is used primarily only in low voltage, low power settings, such as residential and some commercial

## Slide 15: Three-Phase Transmission Line

## Slide 16: Power System Models Needed for the Power Flow
The next few slides introduce the common models of the major electric grid components used for static analysis
  Transmission Lines
  Transformers
  Generators
  Loads
Remainder of this section then explains the process of assembling models of large-scale electric grids for planning studies
Power flow is covered in the next two talks

## Slide 17: Transmission and Distribution
Goal is to move electric power from generation to load with low losses
Less losses at high voltages, but more difficult to insulate
Typical transmission voltages levels are (line-to-line) 765, 500, 345, 230, 161, 138, 115, 69 kV
The highest voltage in North America is 765 kV, but China has a 1000 kV grid
Lower voltages are used for distribution (12.4, 13.8 kV); Transformers used to change voltages
Typical losses are 3 to 5% in transmission and 10 to 15% in the distribution system

## Slide 18: Transmission and Distribution
Transmission
  networked connections
  power can be supplied from multiple sources
  voltage 69 kV and above
  mostly overhead, with some underground in urban areas
  Usually source of large-scale blackouts
Distribution
  radial connections
  power moves in one direction only
  voltage below 69 kV
  the source of most blackouts, but these are local
  Most new construction is underground, especially in suburban and urban locations

## Slide 19: One-line Diagrams
Most high voltage power systems are modeled as balanced three-phase systems
A balanced three-phase system can be represented as a single (or one) line diagram
Onelines show the major power system components such as generators, loads, transmission lines, and transformers
Components join together at a bus
Substation bus

## Slide 20: Transmission Lines
Given the short course focus on power flow, we’ll quickly go through an overview of transmission line, transformer, generator and load modeling
  Our focus is on how to use the models to study power systems in tools such as power flow
Transmission lines are the primary method for long distance electric power transfer
  Overhead ac
  Underground ac
  HVDC – overhead or underground

## Slide 21: 345 kV+ Transmission Growth at a Glance

## Slide 22: 345 kV+ Transmission Growth at a Glance

## Slide 23: 345 kV+ Transmission Growth at a Glance

## Slide 24: 345 kV+ Transmission Growth at a Glance

## Slide 25: 345 kV+ Transmission Growth at a Glance

## Slide 26: HVDC Lines in North America
http://www.grainbeltexpresscleanline.com/site/page/history_of_hvdc_transmission

## Slide 27: Line Conductors
Typical transmission lines use multi-strand conductors
ACSR (aluminum conductor steel reinforced) conductors are most common. A typical Al to steel ratio is about 4 to 1.
AAC (all aluminum conductors) are lighter but have less strength; used in urban areas with shorter spans
Copper is heavier, but has better conductance; used in cables where weight is not an issue
Total conductor area is given in circular mils. One circular mil is the area of a circle with a diameter of 0.001 =   0.00052 square inches
Because conductors are stranded, the equivalent radius must be provided by the manufacturer. In tables this value is known as the geometric mean radius (GMR) and is usually expressed in feet.

## Slide 28: Transmission Line Parameters
We'll quickly cover how to calculate transmission line parameters, which will then form part of the input to our power system model, such as in PowerWorld:
  Resistance
  Inductance
  Capacitance
  Ampacity

## Slide 29: Line Resistance
Line resistance per unit length is given by
where is the resistivity
Resistivity of Copper =
Resistivity of Aluminum =
Example: resistance in / mile of a 1” diameter solid aluminum wire (at dc)
Because ac current tends to flow towards the surface of a conductor, the resistance of a line at 60 Hz is slightly higher than at dc; resistivity and hence line resistance change with conductor temperature (change is about 0.4% per degree C)
  Because ACSR conductors are stranded, actual resistance, inductance and capacitance needs to be determined from tables.

## Slide 30: Recall, Power System Components
Major Components:
  Generators
    Power conversion technology, regulation and control
  Transmission System (69 kV and above)
    Substations, transmission lines, power transformers, control devices
  Distribution System (below 69 kV)
    Distribution feeders, service transformers, metering and control
  Loads
    Customer electricity demands, patterns, quality

## Slide 31: Voltage Levels Usage Table
These voltages are measured Line-to-Line (except single phase LV)
Recall, Line-to-Neutral is less by a factor of
Many voltages are in use in U.S. power systems—here are some of the main ones.
"High Voltage", "Low Voltage" are relative terms, sometimes all can be labeled "High Voltage"
The labels given are typical for power system analysis
Level | Typical Voltages | Usage
Low Voltage | 120 V, 208 V, 240 V, 600 V | Customer-level loads, residential, commercial, smaller industrial
Medium Voltage | 4.16 kV, 12.47 kV, 13.8 kV, 20 kV, 22 kV, 34.5 kV | Distribution feeders, generator step-up, larger industrial motors
High Voltage | 69 kV, 100 kV, 115 kV, 138 kV, 161 kV, 230 kV | Transmission system network
Extra High Voltage (EHV) | 345 kV, 500 kV, 765 kV | Backbone of large transmission systems

## Slide 32: Transmission Line Models
Transmission lines will be modeled using the p circuit
This model is only valid for transmission lines with symmetric tower configurations or if one assumes uniformly transposed lines

## Slide 33: Symmetric Line Spacing – 69 kV

## Slide 34: Transposition
To keep system balanced, over the length of a transmission line the conductors are rotated so each phase occupies each position on tower for an equal distance. This is known as transposition.
In practice, not all lines are transposed, but it is a very common assumption for simplicity of calculation
Aerial or side view of conductor positions over the length of the transmission line.

## Slide 35: Conductor Bundling
To increase the capacity of high voltage transmission lines it is very common to use a number of conductors per phase. This is known as conductor bundling. Typical values are two conductors for 345 kV lines, three for 500 kV and four for 765 kV.

## Slide 36: Bundled Conductor Pictures
Photo Source: BPA and American Electric Power
The AEP Wyoming-Jackson Ferry 765 kV line uses 6-bundle conductors. Conductors in a bundle are at the same voltage!

## Slide 37: Transmission Line Series Compensation
One way to increase the transmission capacity of a transmission line that is limited by its reactance is to add series compensation
  Capacitors are placed in series with the transmission line (covered in Example 5.10)
Image: https://www.bpa.gov/news/newsroom/Pages/Chief-engineers-reunite-reminisce-for-BPAs-75th.aspx
Image shows BPA series capacitors in a 500 kV line

## Slide 38: Transmission Line Series Compensation
Amount of series compensation is expressed as a percentage of the total line reactance (e.g., 50%)
The series capacitance is usually setup so that it can be bypassed sometimes
  There can be excessive reactive power generation on the system during light loads, like at night
There can be a concern with sub-synchronous interactions (SSI)

## Slide 39: Transformers Overview
Power systems are characterized by many different voltage levels, ranging from 765 kV down to 240/120 volts.
Transformers are used to transfer power between different voltage levels.
The ability to inexpensively change voltage levels is a key advantage of ac systems over dc systems.
In this section we’ll development models for the transformer and discuss various ways of connecting three phase transformers.

## Slide 40: Transmission Level Transformer

## Slide 41: Simplified Equivalent Circuit
Often the shunt elements are assumed to have such high impedance that they are ignored

## Slide 42: Residential Distribution Transformers
Single phase transformers are commonly used in residential distribution systems. Most distribution systems are 4 wire, with a multi-grounded, common neutral.
Image: www.osha.gov/dte/library/electrical/electrical_10.gif

## Slide 43: How Do We Deal with Transformers On a Large System?
With many transformers, the equations of the form v1=a*v2 would be everywhere
The per-unit system was designed to make hand calculations and early computer calculations easier.
  Divide all numerical values by a "base" value, i.e. normalize them
  Instead of voltages in V, currents in A, impedance in Ohms, all are given in per-unit.
  Ideal transformers go away in the per-unit system
  Per-unit system has other advantages as well, and is extremely common in industry

## Slide 44: Per Unit Calculations
A key problem in analyzing power systems is the large number of transformers.
  It would be very difficult to continually have to refer impedances to the different sides of the transformers
This problem is avoided by a normalization of all variables.
This normalization is known as per unit analysis.

## Slide 45: Per Unit Conversion Procedure, Single-Phase
Pick a single-phase VA base for the entire system,
Pick a voltage base for each different voltage level, . Voltage bases are related by transformer turns ratios. Voltages are line to neutral.
Calculate the impedance base,
Calculate the current base,
Convert actual values to per unit
Note, per unit conversion on affects magnitudes, not
the angles. Also, per unit quantities no longer have
units (i.e., a voltage is 1.0 p.u., not 1 p.u. volts)

## Slide 46: Per Unit Solution Procedure
Convert to per unit (p.u.) (many problems are already in per unit)
Solve
Convert back to actual as necessary

## Slide 47: Per Unit Example
Solve for the current, load voltage and load power in the circuit shown below using per unit analysis with an SB of 100 MVA, and voltage bases of 8 kV, 80 kV and 16 kV.
Original Circuit

## Slide 48: Per Unit Example, cont’d
Same circuit, with
values expressed
in per unit.

## Slide 49: Per Unit Example, Cont’d

## Slide 50: Per Unit Example, cont’d
To convert back to actual values just multiply the
per unit values by their per unit base

## Slide 51: Three Phase Per-Unit
Procedure is very similar to 1 phase except we use a 3 phase VA base, and use line to line voltage bases
Pick a 3 VA base for the entire system
Pick a voltage base for each different voltage level, VB. Voltages are line to line.
Calculate the impedance base
Exactly the same impedance bases as with single phase!

## Slide 52: Three Phase Per-Unit, cont'd
Calculate the current base, IB
Convert actual values to per unit
Exactly the same current bases as with single phase!
But, be careful in using 3ph bases to calculate it (need a root 3)

## Slide 53: Per Unit Change of MVA Base
Parameters for equipment are often given using power rating of equipment as the MVA base
To analyze a system all per unit data must be on a common power base

## Slide 54: Per Unit Change of Base Example
A 54 MVA transformer has a leakage reactance of 3.69%. What is the reactance on a 100 MVA base?

## Slide 55: Three Phase Transformers
There are 4 different ways to connect 3 transformers: Y-Y, D-D, Y-D, D-Y
  The reasons have to do with grounding and harmonics, which are outside of this short course scope
  Only Y connections can be grounded
  Mixing Y and D introduces a 30 degree phase shift
Most high voltage generator step-up transformers (GSUs) are D on the generator side, grounded Y on the transmission side
Most transmission to distribution is D on the transmission side, grounded Y on the distribution side

## Slide 56: Autotransformers
Autotransformers are transformers in which the primary and secondary windings are coupled magnetically and electrically.
This results in lower cost, and smaller size and weight.
Most transmission level transformers are autotransformers, connected Y-Y with the low side grounded
The key disadvantage is loss of electrical isolation between the voltage levels; not used when a is large. For example in stepping down 7160/240 V we do not ever want 7160 on the low side!

## Slide 57: Three Winding Transformers
Many high voltage transformers have a third winding, called the tertiary winding; called three winding transformers
There are a number of benefits in having 3 windings
  Tertiary can be used to provide lower voltage electric service, including providing substation service for remote transmission substations; sometimes capacitors are connected to the tertiary
  Helps with fault protection by reducing the zero sequence current providing higher zero sequence currents (beyond short course scope)
  When D-connected helps to reduce unbalanced and third harmonic issues (again beyond short course scope)

## Slide 58: Load Tap-Changing Transformers
LTC transformers have tap ratios that can be varied to regulate bus voltages
  Sometimes called on-load tap-changing transformers (OLTCs) or under-load tap-changing transformers (ULTCs)
The typical range of variation is 10% from the nominal values, usually in 33 discrete steps (0.0625% per step).
Because tap changing is a mechanical process, LTC transformers usually have a time delay deadband to avoid repeated changes (e.g., 30 seconds)
Unbalanced tap positions can cause “circulating vars”

## Slide 59: Phase Shifting Transformers
Phase shifting transformers are used to control the phase angle across the transformer
  Also called phase angle regulators (PARs) or quadrature booster transformers (British usage)
Since power flow through the transformer depends upon phase angle, this allows the transformer to regulate the power flow through the transformer
Phase shifters can be used to prevent inadvertent "loop flow" and to prevent line overloads.
Image Source: en.wikipedia.org/wiki/Quadrature_booster#/media/File:Qb-3ph.svg

## Slide 60: Phase Shifter Example: Lake Erie Loop Flow
There are five phase shifters (called phase angle regulators [PARs] here) at the border between Michigan and Ontario. They are used to control how much electricity travels between the US and Canada
By adjusting the PARs the flow of electricity that “loops” around Lake Erie can be controlled
Source: MISO Board of Directors Market Committee Update, 9/30/13

## Slide 61: Modeling Generators and Loads for Power Flow
Generators
Engineering models depend upon application
Generators are usually synchronous machines
For generators we will use two different models:
  a short term model treating the generator as a constant voltage source behind a possibly time-varying reactance
  a steady-state model, treating the generator as a constant power source operating at a fixed voltage; this model will be used for power flow and economic analysis
Loads
Ultimate goal is to supply loads with electricity at constant frequency and voltage
Electrical characteristics of individual loads matter, but usually they can only be estimated
  Actual loads are constantly changing, consisting of a large number of individual devices
  Only limited network observability of load characteristics
Aggregate models are typically used for analysis
Two common models
  Constant power: Si = Pi + jQi
  Constant impedance: Si = |V|2 / Zi

## Slide 62: Questions?