## Slide 1: Fundamentals of Electric Transmission System Planning Short Course Impact of Distributed Energy Resources on Planning
Scott Dahman
PowerWorld Corporation
scott@powerworld.com
March 19-21, 2024
© copyright Tracy Rolstad, 2024
© copyright Scott Dahman, 2024

## Slide 2: Load Records in Power Flow Cases
In system planning tools like PowerWorld Simulator, PSS/E, PSLF, a “load” usually represents a distribution feeder or group of feeders
Distributed Energy Resources (DER) should thus be modeled with the load
Load records in PowerWorld Simulator contain DER fields
  User Input
    Dist Status: Open or Closed – is the DER in service?
    Dist MW: MW output of DER
    Dist Mvar: Mvar output of DER
    Unit Type: typically PV for rooftop solar, but could also be WT, IC, or any other EIA-recognized prime mover type
  Calculated
    Net MW: Load MW – Dist MW
    Net Mvar: Load Mvar – Dist Mvar
The power flow just “sees” the Net MW and Net Mvar
Transient stability can limit or trip the DER separately from the rest of the load

## Slide 3: Transient Stability Load Model Relationship

## Slide 4: DER Transient Stability Load Models
Supported by PowerWorld Simulator
  Specified separately from load characteristic and distribution equivalent (feeder) models
  GE PSLF also recently added, but it is lumped in with load characteristic and feeder models
  Siemens PTI development is in progress
DGDER_A
  Identical to generator machine model DER_A
  Essentially a plant, machine, and electrical model with voltage and frequency tripping characteristics
DGPV: current is limited when voltage or frequency are not within a specified range
Use in industry cases (FERC 715)???
  If there is no DG stability model -> load characteristic model applies to the net

## Slide 5: DER Records in WECC 24HSP1a
Included mainly in California and Arizona

## Slide 6: Transient Stability Model: DGDER_A

## Slide 7: Transient Stability Model: DGPV

## Slide 8: Seminar Time
What experiences do you have?
My experience
  Never integrate load on a generation feeder
    Get them separate
    New generation has no behavior experience
      Good utility practice says what to do
        Not what not to do!

## Slide 9: The Fear Writ Large

## Slide 10: DER IS Coming
We need a robust system
Distributed Energy Resources
  Solar, wind, micro/pico hydro
  MUST INCLUDE STORAGE (& inverter behavior)
    Batteries
      Various kinds are?
    Residential thermal storage
      Which is what? Thoughts?
Transactive grid is a thing…

## Slide 11: Technically Doable
We can do DER but:
  It might be expensive
  It may forever change the utility model
  Rates must accommodate the impact on those unable to buy into DER
    The poor may be the only ones left to pay for energy
      The rich likely HAVE DER

## Slide 12: Modeling Approaches
Do something similar to a FERC SIL study
  Decrement your generation off and run ctgs
    Guarantee you will go “what the?”
Do the same with load
  Decrement your load (i.e. towards zero)
  OR increment the DG components of load
  Run studies and ponder the results

## Slide 13: OATI Graphic (selling software)

## Slide 14: Scale is Everything
We can accommodate DER but at what pace and scale is unknown.
  California is leading the way…pay attention
  Communications and a market are key
The fundamentals are always the same:
  Control of voltage and current (i.e. power)
    Ramping rates
Who is it for reliability?
PMU’s may become very relevant

## Slide 15: OUTUS is Worth Watching
Australia
  VisBlue
Germany
  Voltstorage

## Slide 16: Vanadium Flow
A vanadium redox flow battery (VRFB) has two separate tanks, one containing a positive electrolyte and one negative electrolyte. Both electrolytes consist of the element vanadium dissolved in sulphuric acid, with the vanadium occurring in different oxidation states (valences).
The battery has a number of battery cells as well. Each of these cells is divided into two chambers separated by a membrane, through which the ions can pass. In each chamber there is a positive or a negative electrode. The two electrolytes are pumped through the cells on their side of the membranes.
The current from the solar panels is fed down into the cells’ electrodes, where it moves electrons from the positive to the negative electrolyte, charging the battery as the liquid flows back into the tank. During discharge, this process is then reversed.
Why is a flow battery desirable over a Li-Ion type?

## Slide 17: Don’t Be First!
Any idea where the VC $ is coming from?
4 quadrant control
Economic “stack” of uses
+P
-P
+Q
-Q

## Slide 18: Seminar Time
Pretty sure I am worn out from talking!
Thoughts Please!
Monetizing DER is a HUGE THING for utilities
  We think data might part of this…
The vertically integrated utility may be a dinosaur

## Slide 19: Questions?